## Timing
| IGNITION STATE | TIMING | Units
1 | Pre-Purge | 6 | Seconds
2 | Trial for Ignition | 90 | Seconds
3 | Ignition Retries | 3
4 | Time Between Ignition Retries | 5 | Min
5 | Flame Stabilization Period | 3 | Seconds
6 | Inter-Purge |  | Seconds
7 | Flame Failure Response Time | 1.5 Seconds (2 second maximum; 1 second minimum) | Seconds
8 | Flame Failure Response Current |  | μA
9 | Post-purge | 26 | Seconds
10 | PS Prove Period | 1 (only during intial ignition) | Second
11 | PS Fault Delay (failed closed) | 120 (when it is supposed to open) | Seconds
12 | PS Fault Delay (failed open) | 30 (when it is supposed to closed) | Seconds
13 | PS Fault Retries | 5
14 | Time Between PS Fault Retries | 2 | Min
15 | Soft Lockout | Retry after 5 minutes
16 | ECO Limit/FV/LDO Lockout | Indefinite (cycle power to restart and reset sequence)
17 | Hardware Error Lockout | Indefinite (self clears if fault clears for at least 15 seconds)
18 | FVS Trip Value | 100 | kΩ
19 | FVS Reset Value | 80 | kΩ
20 | LDO Trip Delta Value | 40 | F

## Error code
LED Flash Sequence | Hard/Soft Lock Out | Number of Tries | Reset Procedure | Control Status | Software Hex Values
“Heartbeat”, alternates bright/dim | NA | NA | NA | Call For Heat (no fault conditions)
None (LED not on or flashing) | NA | NA | NA | Electrical Power Not Present
LED lit continuously | Hard Lock Out | NA | NA | Hardware Fault Lockout
One short flash once every four seconds | NA | NA | NA | Idle (no call for heat, no fault conditions)
Short flash once every second (Idle mode) | NA | NA | NA | Low Flame Signal (control continues to operate)
Two Flashes, three second pause | Soft Lock Out | NA | NA | Pressure Switch Failed Closed
Three Flashes, three second pause | Soft Lock Out | NA | NA | Pressure or Temperature Switch Failed Open
Four Flashes, three second pause | Hard Lock Out | NA | Power Cycle and reset procedure | ECO (Energy Cut Off) Limit Lockout. Thermostat Temperature Limit Was Exceeded
Five Flashes, three second pause | Soft Lock Out | NA | NA | Flame Out Of Sequence
Six Flashes-One Flash , three second pause | Soft Lock Out | Three (3) retries. Five minutes between trial for ignition. Hard lockout after 3 failures. | Power Cycle | Soft Lockout - Retry Limit - Failed Trial For Ignition
Six Flashes -Two Flashes, three second pause | Hard Lock Out | After Five (5) recycle due to PS | Power Cycle | Hard Lockout - Recycle Limit - Blower Pressure Switch/Temperature Switch Opened
Six Flashes -Three Flashes, three second pause | Hard Lock Out | After Four (4) recycle | Power Cycle | Hard Lockout - Recycle Limit - Flame Not Established
Six Flashes -Four Flashes, three second pause | Soft Lock Out | 5 Minutes | Power Cycle Will Clear Soft Lockout | Soft Lockout - Flame out of Sequence Sensed. Will Continue Retries Every 5 Minutes.
Six Flashes -Five Flashes, three second pause | Hard Lock Out | After three (3) retries | Power Cycle | Hard Lockout - Retry Limit - Flame Lost
Seven Flashes, three second pause | Hard Lock Out | NA | Power Cycle and reset procedure | Flammable Vapor Sensor (FVS) Lockout
Eight Flashes -One Flash, three second pause | Hard Lock Out | NA | Power Cycle and reset procedure | Flammable Vapor Sensor (FVS) Fault Detected
Eight Flashes -Two Flashes, three second pause | Hard Lock Out | NA | Fix issue and then Power Cycle | Gas Thermostat Temperature Sensor Fault Detected
Eight Flashes -Three Flashes, three second pause | Hard Lock Out | NA | Fix issue and then Power Cycle | Electronics Fault Detected
Eight Flashes -Four Flashes, three second pause | Hard Lock Out | NA | Fix issue and then Power Cycle | Valve Fault Detected
Nine Flashes - one flash, three second pause | Hard Lock Out | NA | Power Cycle and reset procedure | Chamber Has Exceeded Maximum Temperature
Nine Flashes -Two Flashes, three second pause | Hard Lock Out | NA | Power Cycle and reset procedure | Defective Door Thermistor
cross reference between the number of blinks and the actual software hex value.