## Sheet1
Faults stamps |  |  |  | Actual Faults (bits) & Fatal faults |  |  | LED Error Code | Hard Lockout? (Burner Turns Off) | Incorporated in GE Valve? | Has GE Modified anything relating to this error? | How do you reset this error? | Brief Description (I don’t fully understand some of the abbreviations)
No. | Monitor Code | Description |  | Bit |  | Description | No. of Blinks
0 | PVOpen | Pilot Drop Fail (Pilot valve failed open) |  | bit 0 (0x0001) | PILOT_DROP_FAIL | Pilot Drop Fail | 8
1 | MVOpen | Temperature High Limit (Main valve failed open) |  | bit 1 (0x0002) | MV_STUCK_OPEN | Temperature High Limit (MV Stuck Open) | 4
2 | AD | AD converter failed |  | bit 2 (0x0004) | AD_OR_MEM_FAULT | A/D or Memory Fault | 7
3 | Memory | Code Flash or RAM failed |  | bit 2 (0x0004) | AD_OR_MEM_FAULT | A/D or Memory Fault | 7
4 | PV_SF_DrvShrt | Pilot Valve drive or Safety Switch drive failed short |  | bit 3 (0x0008) | PVSFSW_SHORT | PV/SF Drive Short | 7
5 | MVDrvShrt | Main Valve drive failed short |  | bit 4 (0x0010) | MV_SHORT | MV Drive Short | 7
6 | LDO | LDO (WV8860 only) |  | bit 5 (0x0020) | LDO | LDO (WV8860 only) | 10
7 | TankLeakage | Tank Leakage |  | bit 6 (0x0040) | TANK_LEAKAGE | Tank Leakage | 6
8 | PV_SF_DrvOpen | Pilot Valve drive or Safety Switch drive failed open |  | bit 7 (0x0080) | PVSFSW_OPEN | PV/SF Drive Open | 7
9 | MVDrvOpen | Main Valve drive failed open |  | bit 8 (0x0100) | MV_OPEN | MV Drive Open | 7
10 | Pot | Setpoint potentiometer failed | <-> | bit 9 (0x0200) | ELECTRONICS | Electronic Hardware fault | 7
11 | DataFlash | Calibration data in Info Flash is corrupted |  | bit 10 (0x0400) | DATA_FLASH | Calibration Data Corrupted | 7
12 | USOpenShrt | Upper water temperature sensor failed short |  | bit 11 (0x0800) | WATER_SENSOR | Water Sensor Failure | 5
13 | SensorDiffRaw | Water temperature sensor reading significantly different |  | bit 11 (0x0800) | WATER_SENSOR | Water Sensor Failure | 5
14 | LSOpenShrt | Lower water temperature sensor failed short |  | bit 11 (0x0800) | WATER_SENSOR | Water Sensor Failure | 5
15 | SensorDiff | Water temperature sensor long-term readings different |  | bit 11 (0x0800) | WATER_SENSOR | Water Sensor Failure | 5
16 | PowerConsump | (not used) |  | bit 12 (0x1000) | POWER_CONSUMPTION | (not used) | 7
17 | ChamberSens | Chamber temperature sensor failed open (WV8860 only) |  | bit 13 (0x2000) | CHAMBER_SENSOR | Chamber Sensor Failure (WV8860 only) | 9
18 | MVClosed | MV Stuck Closed (Insufficient heating) (WV8860 only) |  | bit 14 (0x4000) | MV_STUCK_CLOSED | MV Stuck Closed (WV8860 only) | 3
19 | Vtp | Low thermopile voltage |  | bit 15 (0x8000) | VTP_LOW | Low Thermopile Voltage | 2
20 | ChamberHW | Chamber sensor electronics failure (WV8860 only) |  | bit 9 (0x0200) | ELECTRONICS | Electronic Hardware fault | 7
Heat | Ambient | Thermowell Rate | Error
TRUE | TRUE | TRUE | No Error
TRUE | TRUE | FALSE | No Error
TRUE | FALSE | TRUE | Error 9
FALSE | TRUE | TRUE | Error 9
FALSE | FALSE | TRUE | Error 9
TRUE | FALSE | FALSE | Error 3
FALSE | TRUE | FALSE | Error 3
FALSE | FALSE | FALSE | Error 3
Any additional errors that are not listed.
If there is an error with the chamber thermistor AND
its heating water, Error 9 Blink
If there is an error with the chamber thermistor AND
its NOT heating water, Error 3 Blink